## VLV22
0.6/1kV-1 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
1X10 | 1 | 0.2 | 1.8 | 12.39 | 227.8705 | 3.08 | 38 | 54
1X16 | 1 | 0.2 | 1.8 | 13.5 | 271.2471 | 1.91 | 51 | 71
1X25 | 1.2 | 0.2 | 1.8 | 15.16 | 339.4396 | 1.2 | 66 | 92
1X35 | 1.2 | 0.2 | 1.8 | 15.8 | 382.826 | 0.868 | 81 | 110
1X50 | 1.4 | 0.2 | 1.8 | 17.5 | 466.1883 | 0.641 | 98 | 130
1X70 | 1.4 | 0.2 | 1.8 | 19.1 | 562.5075 | 0.443 | 120 | 160
1X95 | 1.6 | 0.2 | 1.8 | 21.1 | 693.5541 | 0.32 | 150 | 195
1X120 | 1.6 | 0.2 | 1.8 | 22.5 | 799.5118 | 0.253 | 180 | 225
1X150 | 1.8 | 0.2 | 1.8 | 24.5 | 948.7116 | 0.206 | 205 | 250
1X185 | 2 | 0.2 | 1.7735 | 26.447 | 1108.8757 | 0.164 | 235 | 285
1X240 | 2.2 | 0.2 | 1.8645 | 29.229 | 1365.0211 | 0.125 | 280 | 330
1X300 | 2.4 | 0.2 | 1.9485 | 31.997 | 1637.627 | 0.1 | 320 | 370
1X400 | 2.6 | 0.5 | 2.127 | 37.254 | 2431.958 | 0.0778 | 380 | 430
1X500 | 2.8 | 0.5 | 2.232 | 41.464 | 2954.3846 | 0.0605 | 440 | 580
1X630 | 2.8 | 0.5 | 2.3405 | 45.081 | 3489.5576 | 0.0469 | 500 | 650
0.6/1kV-2 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
2X2.5 | 0.8 | 0.2 | 1.8 | 13.5 | 251 | 12.1 | - | -
2X4 | 1 | 0.2 | 1.8 | 15.3 | 311 | 7.41 | - | -
2X6 | 1 | 0.2 | 1.8 | 16.3 | 352 | 4.61 | - | -
2X10 | 1 | 0.2 | 1.8 | 18.98 | 447.4281 | 3.08 | 38 | 54
2X16 | 1 | 0.2 | 1.8 | 21.2 | 548.9186 | 1.91 | 51 | 71
2X25 | 1.2 | 0.2 | 1.8 | 24.52 | 711.7 | 1.2 | 66 | 92
2X35 | 1.2 | 0.2 | 1.8 | 25.8 | 810.1568 | 0.868 | 81 | 110
2X50 | 1.4 | 0.2 | 1.854 | 29.308 | 1018.6389 | 0.641 | 98 | 130
2X70 | 1.4 | 0.2 | 1.952 | 32.704 | 1264.2502 | 0.443 | 120 | 160
2X95 | 1.6 | 0.5 | 2.148 | 38.896 | 2032.8761 | 0.32 | 150 | 195
2X120 | 1.6 | 0.5 | 2.2481 | 41.8962 | 2343.0891 | 0.253 | 180 | 225
2X150 | 1.8 | 0.5 | 2.372 | 45.944 | 2777.129 | 0.206 | 205 | 250
2X185 | 2 | 0.5 | 2.519 | 50.638 | 3319.0946 | 0.164 | 235 | 285
0.6/1kV-3 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X2.5 | 0.8 | 0.2 | 1.8 | 14.3 | 276 | 12.1 | - | -
3X4 | 1 | 0.2 | 1.8 | 16.1372 | 346.9812 | 7.41 | - | -
3X6 | 1 | 0.2 | 1.8 | 17.2578 | 396.7561 | 4.61 | - | -
3X10 | 1 | 0.2 | 1.8 | 19.9084 | 510.182 | 3.08 | 38 | 54
3X16 | 1 | 0.2 | 1.8 | 22.3005 | 634.1092 | 1.91 | 51 | 71
3X25 | 1.2 | 0.2 | 1.8 | 25.8778 | 833.0168 | 1.2 | 66 | 92
3X35 | 1.2 | 0.2 | 1.786 | 27.2289 | 960.5046 | 0.868 | 81 | 110
3X50 | 1.4 | 0.2 | 1.9145 | 31.1495 | 1228.9302 | 0.641 | 98 | 130
3X70 | 1.4 | 0.2 | 2.0343 | 35.2371 | 1576.9462 | 0.443 | 120 | 160
3X95 | 1.6 | 0.5 | 2.2275 | 41.349 | 2431.562 | 0.32 | 150 | 195
3X120 | 1.6 | 0.5 | 2.3356 | 44.5823 | 2823.9143 | 0.253 | 180 | 225
3X150 | 1.8 | 0.5 | 2.4834 | 49.3724 | 3424.1802 | 0.206 | 205 | 250
3X185 | 2 | 0.5 | 2.6271 | 53.9697 | 4044.7913 | 0.164 | 235 | 285
3X240 | 2.2 | 0.5 | 2.8376 | 60.6093 | 5046.7178 | 0.125 | 280 | 330
3X300 | 2.4 | 0.5 | 3.0191 | 66.3597 | 6023.6363 | 0.1 | 320 | 370
0.6/1kV-4 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X2.5 | 0.8 | 0.2 | 1.8 | 14.9 | 320 | 12.1 | - | -
4X4 | 1 | 0.2 | 1.8 | 17.2354 | 396.4471 | 7.41 | - | -
4X6 | 1 | 0.2 | 1.8 | 18.4906 | 457.1788 | 4.61 | - | -
4X10 | 1 | 0.2 | 1.8 | 21.4599 | 597.1566 | 3.08 | 38 | 54
4X16 | 1 | 0.2 | 1.8 | 24.1394 | 747.1429 | 1.91 | 51 | 71
4X25 | 1.2 | 0.2 | 1.7756 | 28.0978 | 989.2822 | 1.2 | 66 | 92
4X35 | 1.2 | 0.2 | 1.8688 | 29.8291 | 1166.0954 | 0.868 | 81 | 110
4X50 | 1.4 | 0.2 | 2.0268 | 34.6489 | 1537.3243 | 0.641 | 98 | 130
4X70 | 1.4 | 0.5 | 2.1873 | 40.0325 | 2326.88 | 0.443 | 120 | 160
4X95 | 1.6 | 0.5 | 2.3567 | 45.4407 | 2950.8647 | 0.32 | 150 | 195
4X120 | 1.6 | 0.5 | 2.4919 | 49.4905 | 3497.5407 | 0.253 | 180 | 225
4X150 | 1.8 | 0.5 | 2.6418 | 54.377 | 4191.2983 | 0.206 | 205 | 250
4X185 | 2 | 0.5 | 2.8167 | 59.9548 | 5035.8247 | 0.164 | 235 | 285
4X240 | 2.2 | 0.5 | 3.0369 | 66.9131 | 6228.6718 | 0.125 | 280 | 330
4X300 | 2.4 | 0.5 | 3.2402 | 73.3546 | 7466.9175 | 0.1 | 320 | 370
0.6/1kV-5 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
5X2.5 | 0.8 | 0.2 | 1.8 | 16.126 | 356.382 | 12.1 | - | -
5X4 | 1 | 0.2 | 1.8 | 18.448 | 459.4909 | 7.41 | - | -
5X6 | 1 | 0.2 | 1.8 | 19.852 | 525.3561 | 4.61 | - | -
5X10 | 1 | 0.2 | 1.8 | 23.173 | 699.7462 | 3.08 | 38 | 54
5X16 | 1 | 0.2 | 1.8 | 26.17 | 870.6868 | 1.91 | 51 | 71
5X25 | 1.2 | 0.2 | 1.854 | 30.76 | 1174.2335 | 1.2 | 66 | 92
5X35 | 1.2 | 0.2 | 1.958 | 32.6959 | 1391.4691 | 0.868 | 81 | 110
5X50 | 1.4 | 0.5 | 2.1746 | 39.3192 | 2224.0011 | 0.641 | 98 | 130
5X70 | 1.4 | 0.5 | 2.3069 | 43.9038 | 2759.7783 | 0.443 | 120 | 160
5X95 | 1.6 | 0.5 | 2.5099 | 50.3798 | 3573.5692 | 0.32 | 150 | 195
5X120 | 1.6 | 0.5 | 2.6422 | 54.4244 | 4180.7271 | 0.253 | 180 | 225
5X150 | 1.8 | 0.5 | 2.8263 | 60.3226 | 5093.3376 | 0.206 | 205 | 250
5X185 | 2 | 0.5 | 3.0059 | 66.0817 | 6056.2404 | 0.164 | 235 | 285
5X240 | 2.2 | 0.5 | 3.2515 | 73.8631 | 7519.9416 | 0.125 | 280 | 330
5X300 | 2.4 | 0.5 | 3.4924 | 81.4947 | 9126.1962 | 0.1 | 320 | 370
0.6/1kV-3+1 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3*4+1*2.5 | 1.0/0.8 | 0.2 | 1.8 | 16.7405 | 383.3391 | 7.41/12.1 | - | -
3*6+1*4 | 1.0/1.0 | 0.2 | 1.8 | 18.2046 | 443.309 | 4.61/7.41 | - | -
3*10+1*6 | 1.0/1.0 | 0.2 | 1.8 | 20.7517 | 561.3877 | 3.08/4.61 | 38 | 54
3*16+1*10 | 1.0/1.0 | 0.2 | 1.8 | 23.5104 | 710.6694 | 1.91/3.08 | 51 | 71
3*25+1*16 | 1.2/1.0 | 0.2 | 1.8 | 27.1949 | 936.6576 | 1.2/1.91 | 66 | 92
3*35+1*16 | 1.2/1.0 | 0.2 | 1.8137 | 28.3839 | 1056.5363 | 0.868/1.91 | 81 | 110
3*50+1*25 | 1.4/1.2 | 0.2 | 1.9535 | 32.8379 | 1378.4889 | 0.641/1.2 | 98 | 130
3*70+1*35 | 1.4/1.2 | 0.5 | 2.1217 | 37.9809 | 2122.8127 | 0.443/0.868 | 120 | 160
3*95+1*50 | 1.6/1.4 | 0.5 | 2.2847 | 42.9655 | 2672.577 | 0.32/0.641 | 150 | 195
3*120+1*70 | 1.6/1.4 | 0.5 | 2.4192 | 47.325 | 3221.4439 | 0.253/0.443 | 180 | 225
3*150+1*70 | 1.8/1.4 | 0.5 | 2.5317 | 50.9983 | 3702.7392 | 0.206/0.443 | 205 | 250
3*185+1*95 | 2.0/1.6 | 0.5 | 2.6947 | 56.1644 | 4471.6625 | 0.164/0.32 | 235 | 285
3*240+1*120 | 2.2/1.6 | 0.5 | 2.9042 | 62.7308 | 5540.3519 | 0.125/0.253 | 280 | 330
3*300+1*150 | 2.4/1.8 | 0.5 | 3.0941 | 68.8582 | 6643.2623 | 0.1/0.206 | 320 | 370
0.6/1kV-4+1 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4*4+1*2.5 | 1.0/0.8 | 0.2 | 1.8 | 17.9836 | 429.3352 | 7.41/12.1 | - | -
4*6+1*4 | 1.0/1.0 | 0.2 | 1.8 | 19.5712 | 507.8457 | 4.61/7.41 | - | -
4*10+1*6 | 1.0/1.0 | 0.2 | 1.8 | 22.5088 | 652.7766 | 3.08/4.61 | 38 | 54
4*16+1*10 | 1.0/1.0 | 0.2 | 1.8 | 25.5706 | 832.3253 | 1.91/3.08 | 51 | 71
4*25+1*16 | 1.2/1.0 | 0.2 | 1.8256 | 29.8069 | 1113.6621 | 1.2/1.91 | 66 | 92
4*35+1*16 | 1.2/1.0 | 0.2 | 1.9088 | 31.3556 | 1279.8633 | 0.868/1.91 | 81 | 110
4*50+1*25 | 1.4/1.2 | 0.5 | 2.1217 | 37.9498 | 2078.4644 | 0.641/1.2 | 98 | 130
4*70+1*35 | 1.4/1.2 | 0.5 | 2.2483 | 42.0046 | 2554.8858 | 0.443/0.868 | 120 | 160
4*95+1*50 | 1.6/1.4 | 0.5 | 2.4456 | 48.2533 | 3315.8368 | 0.32/0.641 | 150 | 195
4*120+1*70 | 1.6/1.4 | 0.5 | 2.5802 | 52.4104 | 3901.0807 | 0.253/0.443 | 180 | 225
4*150+1*70 | 1.8/1.4 | 0.5 | 2.714 | 56.782 | 4529.1287 | 0.206/0.443 | 205 | 250
4*185+1*95 | 2.0/1.6 | 0.5 | 2.9095 | 63.0269 | 5549.2823 | 0.164/0.32 | 235 | 285
4*240+1*120 | 2.2/1.6 | 0.5 | 3.133 | 70.0621 | 6827.9133 | 0.125/0.253 | 280 | 330
4*300+1*150 | 2.4/1.8 | 0.5 | 3.3619 | 77.3459 | 8279.4222 | 0.1/0.206 | 320 | 370
0.6/1kV-3+2 core aluminum conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3*4+2*2.5 | 1.0/0.8 | 0.2 | 1.8 | 17.5192 | 410.0516 | 7.41/12.1 | - | -
3*6+2*4 | 1.0/1.0 | 0.2 | 1.8 | 19.2904 | 494.6134 | 4.61/7.41 | - | -
3*10+2*6 | 1.0/1.0 | 0.2 | 1.8 | 21.8446 | 621.1858 | 3.08/4.61 | 38 | 54
3*16+2*10 | 1.0/1.0 | 0.2 | 1.8 | 24.9712 | 797.2637 | 1.91/3.08 | 51 | 71
3*25+2*16 | 1.2/1.0 | 0.2 | 1.8803 | 28.9118 | 1057.8178 | 1.2/1.91 | 66 | 92
3*35+2*16 | 1.2/1.0 | 0.2 | 1.9166 | 30.0212 | 1177.7458 | 0.868/1.91 | 81 | 110
3*50+2*25 | 1.4/1.2 | 0.2 | 2.0988 | 35.5916 | 1602.8573 | 0.641/1.2 | 98 | 130
3*70+2*35 | 1.4/1.2 | 0.5 | 2.2504 | 40.2268 | 2364.5129 | 0.443/0.868 | 120 | 160
3*95+2*50 | 1.6/1.4 | 0.5 | 2.4337 | 45.8315 | 3014.9538 | 0.32/0.641 | 150 | 195
3*120+2*70 | 1.6/1.4 | 0.5 | 2.5876 | 50.5352 | 3644.6945 | 0.253/0.443 | 180 | 225
3*150+2*70 | 1.8/1.4 | 0.5 | 2.6953 | 53.8287 | 4109.7347 | 0.206/0.443 | 205 | 250
3*185+2*95 | 2.0/1.6 | 0.5 | 2.9021 | 60.1502 | 5090.4458 | 0.164/0.32 | 235 | 285
3*240+2*120 | 2.2/1.6 | 0.5 | 3.1081 | 66.4482 | 6195.4241 | 0.125/0.253 | 280 | 330
3*300+2*150 | 2.4/1.8 | 0.5 | 3.3217 | 72.9774 | 7420.7443 | 0.1/0.206 | 320 | 370